{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["建筑物年预计雷击次数计算"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"建筑物年预计雷击次数计算","index":0,"n_rows":29,"n_cols":24,"rows_kept":29,"merged":[[0,0,0,9],[0,13,0,22],[1,0,2,0],[1,1,2,1],[1,2,1,4],[1,13,2,13],[1,14,2,14],[1,15,1,17],[6,0,6,10],[6,13,6,23],[7,0,8,0],[7,1,8,1],[7,2,7,4],[7,13,8,13],[7,14,8,14],[7,15,7,17],[12,0,12,9],[12,13,12,22],[13,0,14,0],[13,1,14,1],[13,2,13,4],[13,13,14,13],[13,14,14,14],[13,15,13,17],[18,0,18,10],[18,13,18,23],[19,0,20,0],[19,1,20,1],[19,2,19,4],[19,13,20,13],[19,14,20,14],[19,15,19,17],[24,0,24,9],[24,13,24,22],[25,0,26,0],[25,1,26,1],[25,2,25,4],[25,13,26,13],[25,14,26,14],[25,15,25,17]],"flags":["formulas_cached_only"]}
["建筑物年预计雷击次数计算（H<100m）",{"$nulls":12},"建筑物年预计雷击次数计算（H≥100m）"]
["序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数",{"$nulls":3},"序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数"]
[null,null,"L/m","W/m","H/m","D/m","Ae/m2","k","Td/天","N/次/a",{"$nulls":5},"L/m","W/m","H/m","H/m","Ae/m2","k","Td/天","N/次/a"]
[1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":20,"d":"20.00"},{"v":60,"d":"60.00"},{"v":0.023909724,"d":"0.0239"},1,34.7,{"v":0.08296674228000002,"d":"0.083"},{"$nulls":3},1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":110,"d":"110.00"},{"v":110,"d":"110.00"},{"v":0.059613239,"d":"0.0596"},1,34.7,{"v":0.20685793933000005,"d":"0.207"}]
[2,{"$nulls":12},2]
[]
["当建筑物的高小于100m， 同时其周边在2D 范围内有等高或比它低的其他建筑物， \n这些建筑物不在所考虑建筑物以hr=100(m)的保护范围内时",{"$nulls":12},"当建筑物的高等于或大于100m， 同时其周边在2H 范围内有等高或比它低的其他建筑物， \n这些建筑物不在所考虑建筑物以滚球半径等于建筑物高( m )的保护范围内时，"]
["序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数","平行长度\n总和",null,null,"序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数","平行长度\n总和"]
[null,null,"L/m","W/m","H/m","D/m","Ae/m2","k","Td/天","N/次/a","L/m",{"$nulls":4},"L/m","W/m","H/m","H/m","Ae/m2","k","Td/天","N/次/a","L/m"]
[1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":20,"d":"20.00"},{"v":60,"d":"60.00"},{"v":0.022109724,"d":"0.0221"},1,34.7,{"v":0.07672074228000002,"d":"0.077"},{"v":60,"d":"60.00"},null,null,1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":110,"d":"110.00"},{"v":110,"d":"110.00"},{"v":0.056313239,"d":"0.0563"},1,34.7,{"v":0.19540693933000003,"d":"0.195"},{"v":60,"d":"60.00"}]
[2,{"$nulls":12},2]
[]
["当建筑物的高小于100m， 同时其四周在2D 范围内都有等高或比它低的其他建筑物时",{"$nulls":12},"当建筑物的高等于或大于100m， 同时其四周在2H 范围内都有等高或比它低的其他建筑物时"]
["序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数",{"$nulls":3},"序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数"]
[null,null,"L/m","W/m","H/m","D/m","Ae/m2","k","Td/天","N/次/a",{"$nulls":5},"L/m","W/m","H/m","H/m","Ae/m2","k","Td/天","N/次/a"]
[1,null,60,30,20,{"v":60,"d":"60.00"},{"v":0.010027431,"d":"0.0100"},1,34.7,{"v":0.034795185570000005,"d":"0.035"},{"$nulls":3},1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":110,"d":"110.00"},{"v":110,"d":"110.00"},{"v":0.02120330975,"d":"0.0212"},1,34.7,{"v":0.07357548483250001,"d":"0.074"}]
[2,{"$nulls":12},2]
[]
["当建筑物的高小于100m， 同时其周边在2D范围内有比它高的其他建筑物时",{"$nulls":12},"当建筑物的高等于或大于100m， 同时其周边在2H 范围内有比它高的其他建筑物时，"]
["序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数","平行长度\n总和",null,null,"序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数","平行长度\n总和"]
[null,null,"L/m","W/m","H/m","D/m","Ae/m2","k","Td/天","N/次/a","L/m",{"$nulls":4},"L/m","W/m","H/m","H/m","Ae/m2","k","Td/天","N/次/a","L/m"]
[1,null,{"v":60,"d":"60.00"},{"v":20,"d":"20.00"},{"v":20,"d":"20.00"},{"v":60,"d":"60.00"},{"v":0.018509724,"d":"0.0185"},1,34.7,{"v":0.06422874228000001,"d":"0.064"},{"v":60,"d":"60.00"},null,null,1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":110,"d":"110.00"},{"v":110,"d":"110.00"},{"v":0.053013239,"d":"0.0530"},1,34.7,{"v":0.18395593933,"d":"0.184"},{"v":60,"d":"60.00"}]
[2,{"$nulls":12},2]
[]
["当建筑物的高小于100 m， 同时四周在2D 范围内都有比它高的的其他建筑物时",{"$nulls":12},"当建筑物的高等于或大于100m， 同时其四周在2H 范围内都有比它高的其他建筑物时"]
["序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数",{"$nulls":3},"序号","建筑物性质","建筑物长宽高",null,null,"扩大宽度","等效面积","校正系数","年平均\n雷暴日数","建筑物预计\n雷击次数"]
[null,null,"L/m","W/m","H/m","D/m","Ae/m2","k","Td/天","N/次/a",{"$nulls":5},"L/m","W/m","H/m","H/m","Ae/m2","k","Td/天","N/次/a"]
[1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":20,"d":"20.00"},{"v":60,"d":"60.00"},0.0018,1,34.7,{"v":0.006246000000000001,"d":"0.006"},{"$nulls":3},1,null,{"v":60,"d":"60.00"},{"v":30,"d":"30.00"},{"v":110,"d":"110.00"},{"v":110,"d":"110.00"},0.0018,1,34.7,{"v":0.006246000000000001,"d":"0.006"}]
[2,{"$nulls":12},2]